## Cost of Genset and Service Cost
Diesel Genset (Indicate Brand) | Prices in Juba (USD) | General Reference for Maintenance of Gensets
12.5 kVA | 4500
15 kVA | 6000 | Genset Maintenance | Good Quality Engine |  | Low Quality Engine
20 kVA | 12000 | Maintenance and Replacement | Frequency of change (h) | Price (USD) | Frequency (hours) | Price (USD)
30 kVA | 18500 | Minor Service | 250 | 20 | 250 | 20
45 kVA | 22500 | Major Service | 1000 | 180 | 1000 | 125
60 kVA | 30000 | Overhaul | 10000 | 30% of new | 5000 | 60% of new
80 kVA | 34000 | Replacement | 35000 | See 'Cost of New Gensets' | 10000 | See 'Cost of New Gensets'
100 kVA | 40000

## Genset Fuel consumption chart
Genset Fuel Consumption chart
Generator |  | Liter/hour
kVA | kW | Load 25% | Load 50% | Load 75% | Load 100%
25 | 20 | 2.3 | 3.4 | 4.9 | 6
38 | 30.4 | 4.2 | 6.8 | 9.1 | 11
50 | 40 | 6 | 8.7 | 12.1 | 15.1
75 | 60 | 6.8 | 11 | 14.4 | 18.1
94 | 75.2 | 9.1 | 12.9 | 17.4 | 23.1
125 | 100 | 9.8 | 15.5 | 21.9 | 28
156 | 124.8 | 11.7 | 18.9 | 26.8 | 34.4
169 | 135.2 | 12.5 | 20.4 | 28.7 | 37
188 | 150.4 | 13.6 | 22.3 | 31.8 | 41.2
219 | 175.2 | 15.5 | 25.7 | 36.7 | 48
250 | 200 | 17.1 | 29.1 | 41.6 | 54.4
288 | 230.4 | 20 | 33.3 | 47.3 | 62.7
313 | 250.4 | 21.6 | 35.9 | 51.4 | 68
375 | 300 | 25.7 | 42.7 | 60.9 | 81.3
438 | 350.4 | 29.9 | 49.5 | 70.7 | 94.9
500 | 400 | 33.6 | 56.3 | 80.5 | 108.1
625 | 500 | 41.6 | 69.9 | 99.8 | 134.9
750 | 600 | 49.9 | 83.2 | 119.1 | 161.8
938 | 750.4 | 61.6 | 103.6 | 148.6 | 201.9
1250 | 1000 | 81.6 | 137.6 | 196.9 | 268.8
1563 | 1250.4 | 101.7 | 171.2 | 245.7 | 335.7
1875 | 1500 | 121.7 | 205.3 | 294.1 | 402.6
2188 | 1750.4 | 141.8 | 238.9 | 342.8 | 469.5
2500 | 2000 | 161.8 | 272.9 | 391.5 | 536.4
2813 | 2250.4 | 181.8 | 306.6 | 440 | 603.3

## Generator System
discount factor (d) | 0.14 |  | h
Cost of generator (USD) | 12000
Cost of 1 L of fuel (USD) | 2
Year | Capital Cost | Generator Working time (hours/year) | Minor Service | Major Service | Fuel Consumption (l/h) | Cost of fuel | Overhaul | Replacement | Discount Factor (d) | Present Worth (USD)
|  |  | 20 USD every 250h | 180 USD every 1000h |  |  | 30% genset cost every 10,000h | New genset every 35,000h
0 | 12000 | 2920 | 233.6 | 525.6 | 5 | 29200 |  |  | 1 | 41959.2
1 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.87719 | 26280
2 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.76947 | 23052.6316
3 |  | 2920 | 233.6 | 525.6 |  | 29200 | 3600 |  | 0.67497 | 22651.5041
4 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.59208 | 17738.2514
5 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.51937 | 15559.8697
6 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.45559 | 13649.0085
7 |  | 2920 | 233.6 | 525.6 |  | 29200 | 3600 |  | 0.39964 | 13411.5088
8 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.35056 | 10502.4688
9 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.30751 | 9212.692
10 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.26974 | 8081.3087
11 |  | 2920 | 233.6 | 525.6 |  | 29200 | 3600 |  | 0.23662 | 7940.6899
12 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.20756 | 6218.3047
13 |  | 2920 | 233.6 | 525.6 |  | 29200 |  | 12000 | 0.18207 | 7639.4859
14 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.15971 | 4784.7835
15 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.1401 | 4197.1785
16 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.12289 | 3681.7355
17 |  | 2920 | 233.6 | 525.6 |  | 29200 | 3600 |  | 0.1078 | 3617.6715
18 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.094561 | 2832.976
19 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.082948 | 2485.0666
20 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.072762 | 2179.883
21 |  | 2920 | 233.6 | 525.6 |  | 29200 | 3600 |  | 0.063826 | 2141.9519
22 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.055988 | 1677.3492
23 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.049112 | 1471.3589
24 |  | 2920 | 233.6 | 525.6 |  | 29200 |  |  | 0.043081 | 1290.6657
[9 empty] | TOTAL COST | 254257.5445

## Solar System
discount factor (d) | 0.14
Cost of solar (USD) | 50000
Cost of Invertor (USD) | 4000
Year | Capital Cost | Preventive and Minor Service and | Major Service | Fuel Consumption (l/h) | Cost of fuel | Overhaul | Replacement | Discount Factor (d) | Present Worth (USD)
|  | Cleaning | _ |  |  | _ | Change invertor every 7 yrs
0 | 50000 | 1500 | 0 | 0 | 0 |  |  | 1 | 51500
1 |  | 1500 | 0 |  | 0 |  |  | 0.87719 | 1315.7895
2 |  | 1500 | 0 |  | 0 |  |  | 0.76947 | 1154.2013
3 |  | 1500 | 0 |  | 0 |  |  | 0.67497 | 1012.4573
4 |  | 1500 | 0 |  | 0 |  |  | 0.59208 | 888.1204
5 |  | 1500 | 0 |  | 0 |  |  | 0.51937 | 779.053
6 |  | 1500 | 0 |  | 0 |  | 4000 | 0.45559 | 2505.726
7 |  | 1500 | 0 |  | 0 |  |  | 0.39964 | 599.456
8 |  | 1500 | 0 |  | 0 |  |  | 0.35056 | 525.8386
9 |  | 1500 | 0 |  | 0 |  |  | 0.30751 | 461.2619
10 |  | 1500 | 0 |  | 0 |  |  | 0.26974 | 404.6157
11 |  | 1500 | 0 |  | 0 |  |  | 0.23662 | 354.9261
12 |  | 1500 | 0 |  | 0 |  |  | 0.20756 | 311.3387
13 |  | 1500 | 0 |  | 0 |  | 4000 | 0.18207 | 1001.3816
14 |  | 1500 | 0 |  | 0 |  |  | 0.15971 | 239.565
15 |  | 1500 | 0 |  | 0 |  |  | 0.1401 | 210.1447
16 |  | 1500 | 0 |  | 0 |  |  | 0.12289 | 184.3375
17 |  | 1500 | 0 |  | 0 |  |  | 0.1078 | 161.6995
18 |  | 1500 | 0 |  | 0 |  |  | 0.094561 | 141.8417
19 |  | 1500 | 0 |  | 0 |  |  | 0.082948 | 124.4225
20 |  | 1500 | 0 |  | 0 |  |  | 0.072762 | 109.1426
21 |  | 1500 | 0 |  | 0 |  | 4000 | 0.063826 | 351.0434
22 |  | 1500 | 0 |  | 0 |  |  | 0.055988 | 83.9817
23 |  | 1500 | 0 |  | 0 |  |  | 0.049112 | 73.6681
24 |  | 1500 | 0 |  | 0 |  |  | 0.043081 | 64.6212
[8 empty] | TOTAL COST | 64558.634

## Graph
Cumulative Cost
Year | Generator | Solar
1 | 41959.2 | 51500
2 | 68239.2 | 52815.7895
3 | 91291.8316 | 53969.9908
4 | 113943.3357 | 54982.448
5 | 131681.5871 | 55870.5685
6 | 147241.4568 | 56649.6215
7 | 160890.4653 | 59155.3475
8 | 174301.9742 | 59754.8034
9 | 184804.443 | 60280.642
10 | 194017.135 | 60741.9039
11 | 202098.4437 | 61146.5197
12 | 210039.1336 | 61501.4457
13 | 216257.4382 | 61812.7844
14 | 223896.9241 | 62814.166
15 | 228681.7076 | 63053.731
16 | 232878.8861 | 63263.8757
17 | 236560.6217 | 63448.2132
18 | 240178.2932 | 63609.9127
19 | 243011.2691 | 63751.7544
20 | 245496.3357 | 63876.177
21 | 247676.2188 | 63985.3196
22 | 249818.1707 | 64336.363
23 | 251495.5199 | 64420.3446
24 | 252966.8788 | 64494.0128
25 | 254257.5445 | 64558.634