## Genset Fuel consumption chart
Genset Fuel Consumption chart
Generator |  | Liter/hour
kVA | kW | Load 25% | Load 50% | Load 75% | Load 100%
25 | 20 | 2.3 | 3.4 | 4.9 | 6
38 | 30.4 | 4.2 | 6.8 | 9.1 | 11
50 | 40 | 6 | 8.7 | 12.1 | 15.1
75 | 60 | 6.8 | 11 | 14.4 | 18.1
94 | 75.2 | 9.1 | 12.9 | 17.4 | 23.1
125 | 100 | 9.8 | 15.5 | 21.9 | 28
156 | 124.8 | 11.7 | 18.9 | 26.8 | 34.4
169 | 135.2 | 12.5 | 20.4 | 28.7 | 37
188 | 150.4 | 13.6 | 22.3 | 31.8 | 41.2
219 | 175.2 | 15.5 | 25.7 | 36.7 | 48
250 | 200 | 17.1 | 29.1 | 41.6 | 54.4
288 | 230.4 | 20 | 33.3 | 47.3 | 62.7
313 | 250.4 | 21.6 | 35.9 | 51.4 | 68
375 | 300 | 25.7 | 42.7 | 60.9 | 81.3
438 | 350.4 | 29.9 | 49.5 | 70.7 | 94.9
500 | 400 | 33.6 | 56.3 | 80.5 | 108.1
625 | 500 | 41.6 | 69.9 | 99.8 | 134.9
750 | 600 | 49.9 | 83.2 | 119.1 | 161.8
938 | 750.4 | 61.6 | 103.6 | 148.6 | 201.9
1250 | 1000 | 81.6 | 137.6 | 196.9 | 268.8
1563 | 1250.4 | 101.7 | 171.2 | 245.7 | 335.7
1875 | 1500 | 121.7 | 205.3 | 294.1 | 402.6
2188 | 1750.4 | 141.8 | 238.9 | 342.8 | 469.5
2500 | 2000 | 161.8 | 272.9 | 391.5 | 536.4
2813 | 2250.4 | 181.8 | 306.6 | 440 | 603.3

## Genset Service costs
General Reference for Maintenance of Gensets
Genset Maintenance | Good Quality Engine |  | Low Quality Engine
Maintenance and Replacement | Frequency of change (h) | Price (SDG) | Frequency (hours) | Price (SDG)
Minor Service | 250 | 340 | 250 | 340
Major Service | 1000 | 3060 | 1000 | 2125
Overhaul | 10000 | 30% of new | 5000 | 60% of new
Replacement | 35000 | See 'Cost of New Gensets' | 10000 | See 'Cost of New Gensets'
1USD = 17SDG

## Generator Stand Alone System
discount factor (d) | 0.1
Cost of generator | 12000
Cost of 1 L of fuel | 1
Year | Capital Cost | Working time (hours/year) | Minor Service | Major Service | Fuel Consumption (l/h) | Cost of fuel | Overhaul | Replacement | Discount Factor (d) | Present Worth
|  |  | 340SDG every 250h | 3,060SDG every 1000h |  |  | 30% genset cost every 10,000h | New genset every 35,000h
0 | 12000 | 5840 | 467.2 | 1051.2 | 5 | 29200 |  |  | 1 | 42718.4
1 |  | 5840 | 467.2 | 1051.2 |  | 29200 | 3600 |  | 0.90909 | 31198.5455
2 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.82645 | 25387.1074
3 |  | 5840 | 467.2 | 1051.2 |  | 29200 | 3600 |  | 0.75131 | 25783.9219
4 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.68301 | 20981.0805
5 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  | 12000 | 0.62092 | 26524.7654
6 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.56447 | 17339.736
7 |  | 5840 | 467.2 | 1051.2 |  | 29200 | 3600 |  | 0.51316 | 17610.7656
8 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.46651 | 14330.3603
9 |  | 5840 | 467.2 | 1051.2 |  | 29200 | 3600 |  | 0.4241 | 14554.3517
10 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.38554 | 11843.273
11 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  | 12000 | 0.35049 | 14972.5386
12 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.31863 | 9787.8289
13 |  | 5840 | 467.2 | 1051.2 |  | 29200 | 3600 |  | 0.28966 | 9940.818
14 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.26333 | 8089.1148
15 |  | 5840 | 467.2 | 1051.2 |  | 29200 | 3600 |  | 0.23939 | 8215.5521
16 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.21763 | 6685.2188
17 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  | 12000 | 0.19784 | 8451.6077
18 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.17986 | 5524.9743
19 |  | 5840 | 467.2 | 1051.2 |  | 29200 | 3600 |  | 0.16351 | 5611.3326
20 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.14864 | 4566.0944
21 |  | 5840 | 467.2 | 1051.2 |  | 29200 | 3600 |  | 0.13513 | 4637.465
22 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.12285 | 3773.6318
23 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  | 12000 | 0.11168 | 4770.7122
24 |  | 5840 | 467.2 | 1051.2 |  | 29200 |  |  | 0.10153 | 3118.7039
[9 empty] | TOTAL COST | 346417.9005

## Solar System
discount factor (d) | 0.1
Cost of solar | 50000
Cost of Invertor | 4000
Year | Capital Cost | Minor Service | Major Service | Fuel Consumption (l/h) | Cost of fuel | Overhaul | Replacement | Discount Factor (d) | Present Worth
|  | Cleaning | _ |  |  | _ | Invertor every 7 yrs
0 | 50000 | 100 | 0 | 0 | 0 |  |  | 1 | 50100
1 |  | 100 | 0 |  | 0 |  |  | 0.90909 | 90.9091
2 |  | 100 | 0 |  | 0 |  |  | 0.82645 | 82.6446
3 |  | 100 | 0 |  | 0 |  |  | 0.75131 | 75.1315
4 |  | 100 | 0 |  | 0 |  |  | 0.68301 | 68.3013
5 |  | 100 | 0 |  | 0 |  |  | 0.62092 | 62.0921
6 |  | 100 | 0 |  | 0 |  | 4000 | 0.56447 | 2314.3431
7 |  | 100 | 0 |  | 0 |  |  | 0.51316 | 51.3158
8 |  | 100 | 0 |  | 0 |  |  | 0.46651 | 46.6507
9 |  | 100 | 0 |  | 0 |  |  | 0.4241 | 42.4098
10 |  | 100 | 0 |  | 0 |  |  | 0.38554 | 38.5543
11 |  | 100 | 0 |  | 0 |  |  | 0.35049 | 35.0494
12 |  | 100 | 0 |  | 0 |  |  | 0.31863 | 31.8631
13 |  | 100 | 0 |  | 0 |  | 4000 | 0.28966 | 1187.624
14 |  | 100 | 0 |  | 0 |  |  | 0.26333 | 26.3331
15 |  | 100 | 0 |  | 0 |  |  | 0.23939 | 23.9392
16 |  | 100 | 0 |  | 0 |  |  | 0.21763 | 21.7629
17 |  | 100 | 0 |  | 0 |  |  | 0.19784 | 19.7845
18 |  | 100 | 0 |  | 0 |  |  | 0.17986 | 17.9859
19 |  | 100 | 0 |  | 0 |  |  | 0.16351 | 16.3508
20 |  | 100 | 0 |  | 0 |  |  | 0.14864 | 14.8644
21 |  | 100 | 0 |  | 0 |  | 4000 | 0.13513 | 554.0353
22 |  | 100 | 0 |  | 0 |  |  | 0.12285 | 12.2846
23 |  | 100 | 0 |  | 0 |  |  | 0.11168 | 11.1678
24 |  | 100 | 0 |  | 0 |  |  | 0.10153 | 10.1526
[8 empty] | TOTAL COST | 54955.5499

## Hybrid
discount factor (d) | 0.1
Cost of generator | 12000
Cost of 1 L of fuel | 1.1
Year | Capital Cost | Working time (hours/year) | Minor Service | Major Service | Fuel Consumption (l/h) | Cost of fuel | Overhaul | Replacement | Discount Factor (d) | Present Worth (Generator) | Present Worth (Solar) | Present Worth (Generator +Solar)
|  |  | 340SDG every 250h | 3,060SDG every 1000h |  |  | 30% genset cost every 10,000h | New genset every 35,000h
0 | 12000 | 2920 | 233.6 | 525.6 | 5 | 16060 |  |  | 1 | 28819.2 | 50100 | 78919.2
1 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.90909 | 15290.1818 | 90.9091 | 15381.0909
2 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.82645 | 13900.1653 | 82.6446 | 13982.8099
3 |  | 2920 | 233.6 | 525.6 |  | 16060 | 3600 |  | 0.75131 | 15341.2472 | 75.1315 | 15416.3787
4 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.68301 | 11487.7399 | 68.3013 | 11556.0413
5 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.62092 | 10443.3999 | 62.0921 | 10505.492
6 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.56447 | 9493.9999 | 2314.3431 | 11808.343
7 |  | 2920 | 233.6 | 525.6 |  | 16060 | 3600 |  | 0.51316 | 10478.2782 | 51.3158 | 10529.5941
8 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.46651 | 7846.2809 | 46.6507 | 7892.9317
9 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.4241 | 7132.9827 | 42.4098 | 7175.3924
10 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.38554 | 6484.5297 | 38.5543 | 6523.084
11 |  | 2920 | 233.6 | 525.6 |  | 16060 | 3600 |  | 0.35049 | 7156.805 | 35.0494 | 7191.8544
12 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.31863 | 5359.1154 | 31.8631 | 5390.9785
13 |  | 2920 | 233.6 | 525.6 |  | 16060 |  | 12000 | 0.28966 | 8347.8957 | 1187.624 | 9535.5196
14 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.26333 | 4429.021 | 26.3331 | 4455.3542
15 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.23939 | 4026.3828 | 23.9392 | 4050.322
16 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.21763 | 3660.348 | 21.7629 | 3682.1109
17 |  | 2920 | 233.6 | 525.6 |  | 16060 | 3600 |  | 0.19784 | 4039.8299 | 19.7845 | 4059.6143
18 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.17986 | 3025.081 | 17.9859 | 3043.0668
19 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.16351 | 2750.0736 | 16.3508 | 2766.4244
20 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.14864 | 2500.0669 | 14.8644 | 2514.9313
21 |  | 2920 | 233.6 | 525.6 |  | 16060 | 3600 |  | 0.13513 | 2759.2582 | 554.0353 | 3313.2935
22 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.12285 | 2066.171 | 12.2846 | 2078.4556
23 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.11168 | 1878.3373 | 11.1678 | 1889.5051
24 |  | 2920 | 233.6 | 525.6 |  | 16060 |  |  | 0.10153 | 1707.5793 | 10.1526 | 1717.7319
[9 empty] | TOTAL COST | 190423.9706 | 54955.5499 | 245379.5205

## Graph
Cumulative Cost
Year | Generator | Hybrid (Generator+Solar)
1 | 42718.4 | 78919.2
2 | 73916.9455 | 94300.2909
3 | 99304.0529 | 108283.1008
4 | 125087.9748 | 123699.4795
5 | 146069.0553 | 135255.5207
6 | 172593.8207 | 145761.0128
7 | 189933.5567 | 157569.3558
8 | 207544.3223 | 168098.9499
9 | 221874.6826 | 175991.8816
10 | 236429.0343 | 183167.274
11 | 248272.3073 | 189690.358
12 | 263244.8459 | 196882.2124
13 | 273032.6748 | 202273.191
14 | 282973.4928 | 211808.7106
15 | 291062.6076 | 216264.0648
16 | 299278.1597 | 220314.3867
17 | 305963.3786 | 223996.4976
18 | 314414.9863 | 228056.1119
19 | 319939.9605 | 231099.1788
20 | 325551.2932 | 233865.6032
21 | 330117.3876 | 236380.5344
22 | 334754.8526 | 239693.8279
23 | 338528.4843 | 241772.2835
24 | 343299.1965 | 243661.7886
25 | 346417.9005 | 245379.5205